April 5, 2019

Request for Proposal: 	RFP0319FACSPR - Annual Inspections, Testing and Maintenance of Fire Protection Sprinkler Systems and Associated Equipment

Addendum # 2

The Request for Proposal (RFP) for the above named project is amended as noted in this Addendum. This Addendum consists of clarification to the Scope of Services and Schedule A.

Clarification to Scope of Services (Section II of RFP)

Under Specific Services, A. Inspections,

Five -Year Internal Inspections Piping Condition and Obstruction Inspection Investigations of Fire Protection Sprinkler Systems

Annual Internal inspections of internal piping condition and obstruction inspection of fire protection sprinkler systems pipes shall be performed every five (5) years as required according to the latest NFPA 25 Edition at the time of annual inspections and all authorities having local jurisdictions. The inspection is for the detection of foreign organic or inorganic material inside the pipe. The inspection shall be performed by opening a connection on a main and the removal of a sprinkler head at the end of a branch line. The old sprinkler head shall not be reused and a new sprinkler head of the same size and rating shall be installed.

See anticipated upcoming 5-year obstruction internal inspection quantities in Schedule A.

If obstructions foreign organic or inorganic materials are found during the internal inspection, a complete flushing program will be conducted to remove all foreign materials from the piping then an obstruction investigation will be performed following the requirements per of the latest NFPA 25 Edition at the time of investigation.

The obstruction investigation will take place at a minimum of four points in the fire protection sprinkler system:

- System valve

- Riser

- Cross main

- Branch line

Clarification to Schedule A

Additional devices and clarification to Eureka High School, Lafayette High School and Selvidge Middle School.

See attached Schedule A_Revised2.

End of Addendum #2