**BOARD OF COUNTY COMMISSIONERS**

**JACKSON COUNTY, FLORIDA**

Project # 2021-11

**Generator Maintenance Services**

**ADDENDUM 1**

**Questions and Answers**

**1. Do you have a required emergency repair response time?**

At minimum, within 3 days. Would be addressed with Hourly Rate pay.

**2. Annual load bank tests.**

Perform (2) hour load bank testing with infrared Heat scan. All recordings will be taken at 15 min intervals during load bank test with Oil and fuel filter changes.

**3. Will oil, coolant and fuel sampling be required and if so what will be the time frame of these samples?**

Yes, on an as needed basis per generator.

**4. On the generator list, we need the KW rating on #2, #3, #4 and #5.**

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | Marianna Plant 1 | 2207 Highway 71 Marianna, FL 32446 | Kohler | 180R0 Z J | 385327 | 180 KW |
| 3 | Wayside Lift Station | 4805 Highway 90 Marianna, FL 32446 | Generac | 11051480100 | 2102951 | 250 KW |
| 4 | Cottondale Plant 2 | 2828 Cartledge Lane Cottondale, FL 32431 | Olympian | D125P1 | E2636A/001 | 125 KW  |
| 5 | Cottondale GST | 2331 Green Circle Parkway Cottondale, FL 32431 | Cummins | DSHAB - 6748800 | A080152620 | 175 KW  |

**5. On the scope of work it lists change air filters, spark plugs and fuel filters as required. Is this a charge that will be in addition to the monthly PM or included.**

For the purposes of the bid it should be included in the monthly service cost. I.e. include the cost in the per month column. When undergoing contract negotiations, a price can be developed separately for this line item if necessary.