CITY OF WESTFIELD

WATER RESOURCES

INVITATION FOR BID

TRAILERED STANBY GENERATOR

BID #2268

PURPOSE OF REQUEST

The City of Westfield (“City”) is requesting Bids for the purpose to identify a qualified Bidder that can provide the City with a trailered standby generator per the attached specifications. The City’s needs are outlined in the following Invitation for Bid (“IFB”).

TIME SCHEDULE.

Bids may be picked up and are due in the Purchasing Department no later than May 20, 2011 at 11:00 am.  If at that time City Hall is closed due to an unforeseeable emergency, the bid opening will be held on the next business day at the same time and place.   Bids must be labeled “Bid 2268 Trailered Standby Generator”.  It is the responsibility of the vendor to ensure delivery to the proper location.

The City will follow the following timetable to the best of our ability, dates may change as needed:

Issue IFB 					May 2, 2011

Deadline for Questions			May 13, 2011

Deadline for Submittal of Bids 		May 20, 2011 @ 11:00 am

Contract					May 30, 2011

INSTRUCTIONS TO BIDDERS.

All Bid questions should be directed to:

City of Westfield

Purchasing

Tammy Tefft, MCPPO

59 Court Street

Westfield, MA  01085

413-572-6254

413-572-1708 fax

t.tefft@cityofwestfield.org

All Bids must be in a sealed envelope and clearly marked in the lower left-hand corner: “IFB #2268 – Trailered Standby Generator”

All Bids must be received by 11:00AM on Friday May 20, 2011, at which time they will be opened. One original and one copy of the Bid must be presented. No faxed or telephone Bids will be accepted. If at the time City Hall is closed for any reason, the bids will be accepted on the next normal business day at the same time and place as stipulated.  The Purchasing Director of the City of Westfield reserves the right to ask any additional questions regarding the bid.

Questions concerning this IFB should be directed, in writing, to the City of Westfield Purchasing Department no later than five (5) business days prior to the due date.

“A bidder may correct, modify, or withdraw a bid by written notice received in the Purchasing Department prior to the time and date set for the bid opening.  After bid opening, a bidder may not change the price or any other provision of the bid in a manner prejudicial to the interests of the governmental body or fair competition”.  MGL, chapter 30B, Section 5.

The submission of a bid will be construed to mean that the bidder is fully informed as to the extent and character of the supplies, materials, or equipment required and a representation that the bidder can furnish the supplies, materials, or equipment satisfactorily in complete compliance with the specifications.

All bidders should include all information on their specific generator including any spec sheets and warranty information above what is required.  In addition bidder must list the service location and any pertinent information the bidder feels would benefit.

The City of Westfield reserves the right to select the firm that best meets the requirements of the City.

The City of Westfield reserves the right to reject any or all bids wholly or in part; to waive technicalities and informalities; to amend and/or cancel bid prior to the time of opening; to make awards in a manner deemed best to the City; to correct any award erroneously made as a result of a clerical error on the part of the City.

The successful bidders shall comply with all applicable Federal, State, and Local laws and regulations.  Purchases made by the City are exempt from Federal excise taxes, and bid prices must exclude any such taxes.  Tax exemption certification will be furnished upon request.

Bid must include all delivery and set up chargers, City of Westfield is not responsible for any additional costs that the bidder failed to note.

The Purchasing Department will notify the firm selected within 60 days of the bid opening of award.

Award will be made to the lowest responsive and responsible bidder offering the lowest price for the equipment.

Bidding procedures and award of contracts will be in accordance with, Chapter 30B, effective May 1, 1990, plus all applicable Federal, State and Local Laws and regulations.

SPECIFICATION

TRAILERED STANDBY GENERATOR

# DESCRIPTION OF WORK

  - Work Included:  Provide labor, materials and equipment necessary to complete the work of this Section, including but not limited to the following:

    - New Trailered Generator standby outdoor diesel fired engine generator set, starting system, local indicators/controls, exhaust system with critical silencer located within an outdoor sound attenuated enclosure, jacket water heater, battery, battery blanket space heater, battery charger, integral double wall diesel belly tank, full tank of fuel, fluids, and other accessories as indicated to form a complete and operational system.

    - UL 96A lightning protection system for the Trailered Generator set.

    - On site functional testing of standby power system with 100% load bank for 1 hour.

    - Coordination with the Owners Representative.

    - All other systems hereinafter specified or indicated herein, complete, leaving ready an electrical system in perfect operating condition.

The Trailered Generator set shall be Kohler Model # 275REOZT or approved equal by Caterpillar or Cummins.

# SUBMITTALS

  - Material and equipment requiring Shop Drawing Submittals shall include but not be limited to:

    - Operation and Maintenance Manuals for the Trailered Engine Generator Set

    - Data sheets for the Portable Cables and Camlok Connector System

# REGULATORY REQUIREMENTS

  - Comply with all applicable federal and state laws, and all local codes, by-laws and ordinances.

  - Where provisions of the Contract Specifications conflict with any codes, rules or regulations, the latter shall govern.  Where the contract requirements are in excess of applicable codes, rules or regulations, the contract provisions shall govern unless the Designer rules otherwise.

  - Title/certificate of origin for the trailer to allow registration of unit with the DMV/RMV.

  - Unless otherwise specified or indicated, materials and workmanship and equipment performance shall conform with the latest edition of the following standards, codes, specifications, requirements and regulations:

    - Massachusetts Electrical Code

    - NEMA –MG21

    - NFPA 110

  - All electrical work shall meet or exceed any other state and local codes and/or authorities having jurisdiction including all other standards indicated herein.

# GUARANTEE/WARRANTY

  - Guarantee Work of this Section in writing for one year following the date of the successful completion and acceptance of the required on-site load bank testing.  The guarantee shall repair or replace defective materials, equipment, workmanship and installation that develop within this period, promptly and to the Owners satisfaction.

    - Provide 24 hour service beginning on the date the project is accepted by the Owner until the termination of the guarantee period. Service shall be at no cost to the Owner.  Service shall be provided by an authorized service organization.  Choice of service organization shall be subject to Designer and the Owners approval.  Submit name and a phone number that will be answered on a 24-hour basis each day of the week, for the duration of the service.

    - Submit copies of equipment and material warranties to Owner before final payment.

    - Provide manufacturer's engineering and technical staff at site to analyze and rectify problems that develop during guarantee period immediately.

# OPERATING, INSTRUCTION AND MAINTENANCE MANUALS

  - Provide (2) two copies of the approved operating and maintenance manual and approved shop drawings, equipment literature, cuts, bulletins, details, equipment and engineering data sheets and typewritten instructions relative to the care and maintenance for the operation of the equipment, all properly indexed.  Each manual shall have the following minimum contents:

    - Table of Contents

    - Introduction

      - Explanation of manual and its purpose and use.

      - Description of the electrical systems.

      - Safety precautions necessary for equipment.

      - Illustrations, schematics and diagrams.

      - Installation drawing.

    - Maintenance

      - Maintenance and lubricating instructions.

      - Replacement charts.

      - Trouble shooting charts for equipment components.

      - Testing instructions for each typical component.

      - Two typed sets of instructions for ordering spare parts.  Each set shall include name, price, telephone number and address of where they may be obtained.

    - Manufacturer's Literature

      - The equipment for which shop drawings have been submitted and approved.

# SERVICE CHARACTERISTICS

A.  	Generator Output Voltage: 12 lead Dual system voltages of 480/277 volt, 3-phase 4-wire with equipment ground, and 208/120, 3-phase 4-wire grounded wye with convertible jumper connection cabling for high and low voltages.

B.   	Utility Voltage: 480V 3P 4W with equipment ground and 208V 3P 4W with equipment ground.

# QUALITY ASSURANCE

  - All work shall comply with the latest editions of the codes as referenced herein.

  - Follow manufacturer's directions for articles furnished, in addition to directions shown on drawings or specified herein.

  - Protect all work, materials, and equipment from damage during process of work.  Replace all damaged or defective work, materials and equipment without additional cost to the Owner.

  - Equipment and materials shall:

    - Where normally subject to Underwriters Laboratory Inc. listing or labeling services, be so listed or labeled.

    - Be without blemish or defect.

    - Be in accordance with the latest applicable NEMA standards.

    - Be products which will meet with the acceptance of all authorities having jurisdiction over the work.  Where such acceptance is contingent upon having the products examined, tested and certified by Underwriters or other recognized testing laboratory, the product shall be so examined, tested and certified.

PART 2 - PRODUCTS

# 2.01  	MANUFACTURERS

  - Product specifications are written in such a manner so as to specify what materials may be used in a particular location or application and therefore do not indicate what is not acceptable or suitable for a particular location or application. As an example:  non-metallic sheathed cable is not specified; therefore, it is not acceptable.

  - For purpose of establishing a standard of quality and not for purpose of limiting competition, the basis of this Specification is upon specified models and types of equipment and materials, as manufactured by specified manufacturers.

  - Where Specifications list manufacturer's names and/or "as approved" or "Equal approved by Owner, other manufacturers equipment will be considered if equipment meets Specification requirements and has all features of the specified items as are considered essential by Owner.

  - All materials shall be new and shall be UL listed.

# 2.02  	WIRING MATERIALS – 2000 VOLTS

  - Provide generator output copper Type W  2000 volt single conductor portable power cables for field connection of  three phase motor loads to the generator output panel bus bars as follows :

- (5) Single conductor # 350mcm cables - 50’-0” long (phase A, B, C, neutral and equipment ground conductor) with a male camlok connector on each cable end. Connectors to be color coded as follows :

- (5) Single conductor # 350mcm cables - 50’-0” long (phase A, B, C, neutral and equipment ground conductor) with a female camlok connector on end only and no connector on the other cable end.

- 100’-0” - 14 gauge SJO umbilical cord for remote start/stop of generator from on site automatic transfer switch. Switch is not part of this scope of work

Camlok connectors to be Crouse Hinds E1017 series or approved equal. Camlok connectors are to be color coded as follows:

Phase A			BLACK

Phase B			RED

Phase C			BLUE

Neutral				WHITE

Equipment Ground		GREEN

  - Exterior of wires shall bear repetitive markings along their entire length indicating conductor size, insulation type and voltage rating.

  - Southwire, General Cable, Allied Wire and Cable or equal shall manufacture wiring materials.

2.04   	STANDBY POWER SYSTEM EQUIPMENT

A.	Scope of Work

1.	It is the intent of this specification to procure an engine-driven generator set that has been prototype tested, factory built, production-tested, and site-tested together with all accessories necessary for a complete installation as specified herein.

2.	Any and all exceptions to the published specifications shall be subject to the approval of the Owner.

3.	The power system shall be furnished by a single manufacturer who shall be responsible for the design, coordination, and testing of the complete system.  The entire system shall be installed as specified herein.

4.	The equipment shall be produced by a manufacturer who has produced this type of equipment for a period of at least 10 years and who maintains a service organization available twenty-four hours a day throughout the year.

5.	The equipment shall be produced by a manufacturer who is ISO 9001 certified for the design, development, production, and service of its complete product line.

B.	General

1.	It is the intent of this specification to procure a generator set system that has been tested during production, and at the final job site. The generator set will be a commercial design and will be complete with all of the necessary accessories as specifications herein. The equipment supplied shall meet the requirements of the National Electrical Code and applicable local codes and regulations.

2.	All equipment shall be new and of current production by a national firm that manufactures the generator sets and controls, transfer switches, and switchgear, and assembles the generator sets as a complete and coordinated system. There will be one-source responsibility for warranty, parts, and service through a local representative with factory-trained servicemen.

C.	Submittals

1.	The generator submittal shall include prototype test certification and specification sheets showing all standard and optional accessories to be supplied; schematic wiring diagrams, interconnection diagrams and instructions for field re-wiring of generator output from 480V wye to 208V wye.  Drawings shall be tailored to this project. Generic shop drawings shall not be reviewed for acceptance.

D.         Testing

1.	To ensure that the equipment has been designed and built to the highest reliability and quality standards, the manufacturer and/or local representative shall be responsible for two separate tests: final production tests and site tests.

3.	Final Production Tests. Each generator set shall be tested under varying loads with guards and exhaust system in place. Tests shall include:

a.		Single-step load pickup

b.		Transient and steady-state governing

c.		Safety shutdown device testing

d.		Voltage regulation

e.		Rated Power @ 0.8 PF

f.		Maximum power

g.	A certified test record sent prior to shipment.

4.	Site Tests. The manufacturer's distribution representative shall perform an installation check, startup, and full load 1-hour duration test utilizing a resistive load bank. The Owner or his designee, regular operators, and the maintenance staff shall be notified of the time and date of the site test. The tests shall include:

a.	Fuel, lubricating oil, and antifreeze shall be checked for conformity to the manufacturer's recommendations, under the environmental conditions present and expected. The contractor shall provide a 100% fuel loaded tank subsequent to the required load testing.

b.	Accessories that normally function while the set is standing by shall be checked prior to cranking the engine.  These shall include: block heaters, battery chargers, alternator strip heaters, etc.

c.	Generator set startup under test mode to check for exhaust leaks, cooling air flow, movement during starting and stopping, vibration during operation, line-to-line voltage and frequency, and phase rotation.

d.	Engine coolant temperature, oil pressure, and battery charge level along with generator set voltage, amperes, and frequency shall be monitored throughout the test.

E.	Warranty and Maintenance

1.	The generator set shall include a standard one year warranty to guarantee against defective material and workmanship in accordance with the manufacturer's published warranty from date of startup.

2.	The generator set manufacturer and its distributor shall maintain a 24-hour parts and service organization.  This organization shall regularly engage in maintenance contract programs to perform preventive maintenance and service on equipment similar to that specified.  A service agreement shall be available and shall include system operation under simulated operating conditions; adjustment to the generator set, transfer switch, and switchgear controls as required, and certification in the owner's maintenance log of repairs made and functional tests performed on all systems.

F.	Standby Power System Equipment	id

1.	The output of the standby power system shall be dual voltage rated to supply 480V or 208V 3-phase 4-wire plus equipment ground.

2.	The standby power system shall not be wired as a separately derived system. The neutral bus shall not be bonded to equipment grounding bus. The frame of the generator and the vehicle trailer shall be bonded to the equipment grounding bus. On board receptacles shall be bonded to the equipment grounding bus. The equipment ground bus shall include hole drilling and mechanical lug for the connection of the equipment grounding conductor from the loads being served.

3.	The generator set shall be capable of starting and operating a 150 HP wound rotor motor with VFD or soft start motor controller at 480V or 208V 3-phase 3-wire and a 3-phase 4-wire resistive lighting and appliance load of 11 KVA/KW with a maximum voltage dip of 20%.

4.	Two output thermal magnetic molded case circuit breakers shall be connected to the generator output as follows.

a. 	400 ampere frame/300 ampere trip to serve a 150Hp 480V 3-phase motor and 11KVA/KW lighting and appliance load via a high/low wye reconfigurable bussed output panel.

b.	800 ampere frame/700 ampere trip to serve a 150Hp, 208V, 3-phase motor and 11KVA/KW lighting and appliance load via a high/low wye reconfigurable bussed output panel.

5.	A reconfigurable electrical high/low wye  output power panel with hinged lockable cover shall be provided to house output load  phase and equipment ground connections .The panel shall be equipped with mechanical lugs (1) 350mcm  per phase, neutral bus bars and (1) 350mcm  equipment ground conductor mounted to the equipment grounding bus bar .

6.	The power panel shall include branch circuit breakers, plugs and outlets with weatherproof snap covers for the following.

a.	Power inlet, 120VAC, 15A (NEMA 5-15P) – Utility Power connection for block heater.

b.	Power inlet, 120VAC, 15A (NEMA a 5-15P) – Utility Power      connection for block heater.

c.         Two 20A GFCI duplex receptacles (NEMA 5-20R) – Convenience power available when generator is running.

d.         Power outlet 15A 250V (NEMA L6-15R) - Convenience power   available when generator is running.

e.	Three phase 4-wire with equipment ground 160KA surge suppression unit with alarm indication and enable/disable switch connected with 3-pole circuit breaker to the generator output.

7.       	The generator shall have the following features.

      - Galvanized steel sound attenuated enclosure with factory painted.

      - Leroy Somer 4-pole alternator, NEMA MG1 insulated

      - Solid State R20 Voltage regulator,+/- 1% regulation no load to full load

      - 251-gallon 110% containment double wall fuel oil tank with leak detection system.

      - Battery in leak proof box, rack disconnect switch and charger with utility power connection plug.

      - Containment pan under engine for containing engine oil and coolant.

      - Block Heater with utility power connection plug

      - Unit mounted radiator with 45ºC (113ºF) ambient air capacity

      - Skid and vibration isolators

      - Microprocessor based controller with emergency stop switch and the following features.

- LCD display panel with three lines of text and icons for system status

- User buttons for start, stop, and menu scroll

- ON/AUTO/OFF key switch feature or equivalent

- Viewable/selectable parameter as follows.

- Mode of operation

- Battery voltage

- Frequency

- Hour meter

- Engine Speed

- % fuel level

- Coolant temperature

- Oil pressure

- Voltage: phase to phase; phase to neutral

- Current

- Viewable Faults as follows.

      - Over speed

      - Over crank

      - Low fuel level

      - Low and high coolant temperature

      - Oil pressure

      - Battery charger

      - Frequency meter, ammeter, voltmeter

      - Emergency Stop

      - Externally mounted emergency stop switch

      - Terminal connection point for remote start/stop control station

      - John Deer Engine, or manufacturer’s standard if other than Kohler unit is approved,  EPA certified to meet Massachusetts Department of Environmental Protection Guidelines

      - All access doors of the sound attenuated housing and power panel shall be equipped with locksets with 10 spare keys provided.

      - Terminal blocks for field wiring of start/stop remote signal wiring from site automatic transfer switch.

8.	The generator shall be mounted on a galvanized steel towing trailer that meets Massachusetts Department of Transportation requirements with the following features.

a.	Trailer capacity – 16,000 lbs

b.	Dual axle Electric Brake System with SAE 7 pin socket and wiring harness for running lights and brakes with battery back-up

c.	Leaf spring suspension system

d.	Lunette eye and safety chains

e.	8-hole steel rim 17.5 x 6 with 215/75R17 LHR tires with spare tire

f.	Front and rear stabilizing jacks

g.	Fire extinguisher

h.	Gross weight with generator not to exceed 14,567 lbs

i.	Tool Box with lug wrench and jack

k.	Portable cable rack

l.	License plate frame

G.	Unit Lightning Protection System

1.	The trailered unit shall be equipped with a lightning protection system, designed and installed by a licensed UL 96A contractor.

2.	Air terminals and down comers shall be mechanically fastened to the generator housing and trailer frame. The system shall be connected to the output power panel equipment grounding bus.

END OF SPECIFICATION

Pricing Page

Must be filled out and submitted with bid.  Failure to do so will result in rejection of bid

Trailered Standby Generator

Must include any cost of set up and delivery, generator must be ready to use and move upon delivery:

$__________________________________________

APPENDIX A

IFB #2268

Bidder Point of Contact List

Bidder must fill out completely

1. Technical Support

Name of Contact: __________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Web Link: ________________________________________________________

2. Maintenance/Warranty Support

Name of Contact: __________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Web Link: ________________________________________________________

3. Billing Support

Name of Contact: __________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Web Link: ________________________________________________________

Appendix B

References

1.

Name of Contact: __________________________________________________

Name of Company: ________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Date of Contract: ________________________  # of Devices ______________

2.

Name of Contact: __________________________________________________

Name of Company: ________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Date of Contract: ________________________  # of Devices ______________

3.

Name of Contact: __________________________________________________

Name of Company: ________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Date of Contract: ________________________  # of Devices ______________

4.

Name of Contact: __________________________________________________

Name of Company: ________________________________________________

Address: _________________________________________________________

Phone: ____________________________ Fax: _________________________

Email: ___________________________________________________________

Date of Contract: ________________________  # of Devices ______________

Form for Bid

Having fully examined, read, and in understanding of the specifications for this job and being familiar with all of the conditions surrounding the proposed work and or supplies, including any addenda for which receipt of is acknowledged below, the undersigned proposes to complete all work as specified in this invitation to bid for the price stated below:

Company Information:

Name		___________________________________

Address		___________________________________

___________________________________

Telephone	___________________________________

Fax		___________________________________

E-Mail		___________________________________

FID #		___________________________________

###### This bid includes addenda numbered: ________________________________

NON-COLLUSION AFFIDAVIT

The undersigned certifies under penalties of perjury that this bid or proposal has been made and submitted in good faith and without collusion or fraud with any other person. As used in this certification, the word “person” shall mean any natural person, business, partnership, corporation, union, committee, club, or other organization, entity, or group of individuals.

_________________________________________________

Signature of individual submitting bid or proposal

_________________________________________________

Name of Company

_________________________________________________

Date

AFFIDAVIT OF COMPLIANCE

_________Massachusetts Corporation

_________	Foreign Corporation

_________	Non-Profit Corporation

_________	Partnership

_________	Sole Proprietorship *

Name of Corporation  _________________________________________

Address                       _________________________________________

_________________________________________

As President, or authorized company officer, of the above named corporation, I do hereby certify that the above named corporation has filed with the State Secretary all certificates and annual reports required by M.G.L. Chapter156B §109 and by Chapter 181 §4

Signed under the penalties of perjury this __________ day of _____________, ________

____________________________________________________________

Signature and Title of Authorized Company Officer

Corporate Seal (affix below):

If a sole proprietorship, you must indicate your status as a sole proprietorship; the person signing this bid shall be deemed to be the sole proprietor and legal entity for the purposed of this bid and contract.

Bid Signature Page

Signature for Individual

_______________________________________   		______________________________

Name of Company						Telephone Number

_______________________________________   		______________________________

Name and Title of Individual Authorized to Sign			Fax Number

_______________________________________   		______________________________

Signature							Date

Signature if Partnership (must be signed by all general partners)

_______________________________________   		______________________________

Name of Partnership						Date

_______________________________________   		______________________________

Name & Title of Partner						Signature

_______________________________________   		______________________________

Name & Title of Partner						Signature

_______________________________________   		______________________________

Name & Title of Partner						Signature

_______________________________________   		______________________________

Telephone Number of Offices					Fax Number of Offices

Use Additional Sheet if Necessary

Signature of Corporation

_______________________________________   		______________________________

Name of Corporation						Date

_______________________________________   		______________________________

Name and Title of Duly Authorized Company Officer		Signature

Affix Corporate Seal Below

_____________________________

Telephone Number

_____________________________

Fax Number

_____________________________

Email Address

_____________________________

FID Number

_____________________________

Signature of Clerk

Please furnish the following additional information:

Incorporated in what state? ____________________

President: __________________________________

Treasurer:__________________________________

Secretary: _________________________________

If you are a foreign (out of state) corporation, are you registered with the Secretary of the Commonwealth in accordance with the provisions of M.G.L. Chapter 156D § 15.03? ____________

If you are selected for this work, you are required, under M.G.L. Chapter 30 §391, to obtain from the Secretary of State, Foreign Corporation Section, a certificate stating that your corporation is registered, and to furnish said certificate to the City of Westfield before award.

ATTESTATION OF TAXES

Any person failing to sign the Attestation of Taxes shall not be allowed to obtain, renew, or extend a license, permit, or public contract.

Pursuant to M.G.L. Chapter 62C, §49A, I hereby certify, under the penalties of perjury, that, to the best of my knowledge and belief, I am in compliance with all the laws of the Commonwealth relating to taxes, reporting of employees and contractors, and withholding and remitting child support.

_________________________________________________

Signature and Title of Authorized Company Officer

_______________________________

Date

Corporate Seal (affix below):

# INSURANCE REQUIREMENTS:

The contractor shall maintain such insurance as will protect him from claims under Workmen's Compensation acts and from claims for damages because of bodily injury, including death, which may arise from and during operations under this contract whether such operations be by himself or by any subcontractor or anyone directly/indirectly employed by either of them.

Public Liability Insurance:  The contractor shall maintain such insurance as will protect him against claims of the public.  The amount of the insurance shall be as follows:

Bodily Injury - $250,000/500,000

Property Damage $100,000, Or $1,000,000 Combined Single Limit

OWNERS LIABILITY INSURANCE:  	$1,000,000/2,000,000

To insure the owner, the City of Westfield, against all claims, the limits should be the same as for public liability.

Prior to starting work on the contract, the contractor shall deposit with the City Purchasing Director, certificates from the insurers clearly stating that the insurance policies required in the above paragraphs have been issued to the contractor.

The contractor agrees to assume all liability for injury or damage to the contractor and any and all persons acting by, through, at the invitation of, or on behalf of the contractor, and to all property and equipment of the contractor whether owned by the contractor or not.

The contractor agrees to indemnify, defend and hold the City of Westfield harmless for any injury or damage to any person or property as a direct or indirect consequence of any aspect of the contractor's operation, which undertaking shall survive the term of the contract.